## Com.ASHRAE - Envelope
2020 NYCECC Tabular Analysis Commercial Building in compliance with Appendix CA (Amendments to ASHRAE 90.1-2016)
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, 5.1.3, 6.1.1.3, 6.4.3.10.1, 7.1.1.3, 8.1.4, 9.1.2, and 10.1.1.3.
ASHRAE Citation | Provision | Item Description | Code Prescriptive Value (ASHRAE) | Proposed Design Value | Supporting Documentation
5.4.3.1 | Continuous Air barriers | Sample text: Continuous air barrier | A continuous air barrier for the opaque buildings envelope shall comply with Section 5.4.3.1. | Sample text: Continuous air barrier - 1/2 inch XPS with all joints sealed according to mfg.'s instructions. | Sample text: A-XXX, sealing details, Air sealing notes (A-XXX)
5.4.3.1.3.b | Materials | Sample text: Materials | Items 1 through 13 listed in this section must comply with the requirements of this section. | Sample text: Plywood with a thickness of not less than 3/8 inch meet the requirements of Section 5.4.3.1.3.b. | Sample text: Notes (A-XXX) Specs (A-XXX)
5.4.3.1.3.c | Assemblies | Sample text: Assemblies | Items 1 through 3 listed in this section must comply with the requirements of this section. | Sample text: Concrete masonry walls that are fully grouted meet the requirements of 5.4.3.1.3.c, provided joints are sealed and the requirements of 5.4.3.1 are met. | Sample text: Notes (A-XXX) Specs (A-XXX)
5.4.3.1.3.a | Air barrier testing | Sample text: Air barrier testing | New buildings 10,000 to 50,000 square feet, and less than or equal to 75 feet in height must show compliance through testing. The thermal envelope of the building must comply with Sections 5.4.3.1 and 5.4.3.2. Pressure differential of 0.3 inch water gauge. Air leakage rate 0.40 cfm/ft2maximum. | Sample text: All air barrier testing to be in accordance with ASTM E 779.Building thermal envelope to be tested to no more than 0.4 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Sample text: Air testing notes (A-XXX)
5.4.3.2 | Air leakage of fenestration and doors | Sample text: Replace curtainwall and glazed entrance doors, Floor 1. | Max Air Leakage Rates: Curtain walls and storefront glazing = 0.06 cfm/sf Commercial glazed swinging entrance doors and revolving doors = 1.0 cfm/sf of door area | Sample text: Curtain walls and storefront glazing = 0.06 cfm/sf Commercial glazed swinging entrance doors and revolving doors = 1.0 cfm/sf of door area | Sample text: Vertical fenestration: A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)
5.4.3.3 | Loading dock weatherseals | Provide weatherseals at loading dock. | Cargo doors and loading dock doors shall be equipped with weatherseals to restrict infiltration when vehicles are parked in doorway. | Sample text: weatherseals provided at loading dock door. | Sample text: See note in general notes (A-XX1).
5.4.3.4 | Vestibules | Sample text: Building Entrance vestibule | Vestibule provided at door separating conditioned space from the exterior. | Sample text: New 10’ deep vestibule @ building entrance. Two sets of swinging doors with self-closers. | Sample text: A-XXX (1st Floor Plan) A-5XX (Schedules) Incl. door closer notes in Comments column of Door Schedule).
5.4.4 | Thermal bridges (Mandatory) | Thermal bridges | Clear-field thermal bridges are identified on drawings and pre-calculated assembly values are from ASHRAE 90.1 Appendix A. Point thermal bridges greater than 8in2 are identified. Linear thermal bridges are outlined in tabular format including each linear thermal bridge type, the aggregate length for each, the relevant detail and cross-section through each thermal bridge, and the Psi-value for each thermal bridge. | Clear-field thermal bridges: all wall, roof and floor assemblies are derived from Appendix A of ASHRAE 90.1 Point thermal bridges: no point thermal bridges are in this design Linear thermal bridges: See Table 1 on sheet EN-3 | Sample text: See EN-3 for tabular format of linear thermal bridges, A-XXX, A-XXX and specifications drawing A-XXX
5.5, Table 5.5-4, 5.8.1.8 | Roof Assembly - Insulation entirely above roof deck | Sample text: New steel-deck roof | Minimum R-33ci | Sample text: Roof Type 1: 7” XPS (R -35) continuous insulation above deck | Sample text: Roof Type 1: A-XXX (Roof Plan) A-XXX (Wall Sections) X-Y/A-XXY (Roof Details)
5.5, Table 5.5-4, 5.8.1.8 | Roof assembly - metal buildings | Sample text: New roof on metal building | Sample text: Minimum R-19 + R-11 LS | Sample text: Roof Type 1: R-19 fiberglass batt cavity insulation plus 3" EPS (R-12) linear system (LS) with continuous insulation (ci) installed below the purlins | Sample text: Roof Type 1: A-XXX (Roof Plan) A-XXX (Wall Sections) X-Y/A-XXY (Roof Details)
5.5, Table 5.5-4, 5.8.1.8 | Roof assembly - attic and other | Sample text: New attic | Sample text: Minimum R-53 | Sample text: Roof Type 1: R -53 | Sample text: Roof Type 1: A-XXX (Roof Plan) A-XXX (Wall Sections) X-Y/A-XXY (Roof Details)
5.5, Table 5.5-4 | Walls, above-grade: Mass | Sample text: 8" CMU wall with continuous rigid insulation and brick veneer. | Sample text: Minimum R-13.25ci | Sample text: 3" Extruded polystyrene (XPS) = R-15 ci | Sample text: Exterior Wall Type X: A-XXX (1st Floor Plan) 2/A-XXX (Wall Details)
5.5, Table 5.5-4 | Walls, above-grade: Metal framed | Sample text: Steel-framed wall, 2x4 framing 16" O.C | Sample text: Minimum R-13 + R-8.5ci | Sample text: R-13 batt insulation installed between framing + R-10 ci installed on the exterior of the building | Sample text: Exterior Wall Type X: A-XXX (1st Floor Plan) 2/A-XXX (Wall Details)
5.5, Table 5.5-4 | Walls, above-grade: Wood framed & other | Sample text: Above-grade wood-framed wall 2x4 framing, 16" o.c. | Sample text: Minimum R-13 + R-4.5ci or R-19 + R-1.5ci | Sample text: Exterior Wall Type 1: R-13 fiberglass batt cavity insulation + 2" EPS (R-8) ci | Sample text: Exterior Wall Type X: A-XXX (1st Floor Plan) 2/A-XXX (Wall Details)
5.5, Table 5.5-4 | Below-grade walls | Sample text: Thermal insulation on the interior of new basement wall. | Sample text: Minimum R-10ci | Sample text: 2" Extruded Polystyrene (XPS) = R-10 | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
5.5, Table 5.5-4 | Floors: Mass | Sample text: Thermal insulation at new concrete floor over garage. | Sample text: Minimum R-16.7ci | Sample text: 3.5" Extruded Polystyrene (XPS) = R-17.5 ci | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
5.5, Table 5.5-4 | Floors: Joist/framing | Sample text: Thermal insulation at new steel-joist floor over unconditioned space. | Sample text: Minimum R-30 | Sample text: Exterior Wall Type 1: R-49 fiberglass batt cavity insulation | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
5.5, Table 5.5-4 | Slab-on-grade floors: Heated slabs | Sample text: Slab-on-grade with radiant heating. | Sample text: Minimum R-15 for 24"below plus R-5ci under full slab | Sample text: R-5ci under full slab, R-15 extending from the top of the footing to 24" below | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
5.5, Table 5.5-4 | Opaque doors, Nonswinging | Sample text: Insulated metal roll-up garage door. | Sample text: Minimum R-4.75 | Sample text: R-5 | Insulated Metal Roll-up Door: A-301-302 (Elevations) A-501 (Schedules)
5.5, Table 5.5-4 | Assembly U-factor, C-factor or F-factor-based method | Sample text: 8" block wall with R-13 batt insulation in metal studs and R-10 continuous exterior insulation | Sample text: Mass wall U = 0.086 | Sample text: U-factor calculated using ASHRAE 90.1-2016 Appendix A Ru - 2.07 (Table A3.1-3, 8" block, 115#) R - 10.5 (Table A3.1-4, 10ci) R - 4.7 (Table A3.1-4, R-13 in 3.5 metal stud) U = 1/(2.07 + 10.5 + 4.7) = 0.058 | Sample text: A-XXX, A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)
5.5.3.7 | Continuous insulation | Parapet design | Parapet shall be wrapped with continuous insulation having minimum R-value equivalent to the adjacent wall assembly. Above-grade wall assembly - 10ci. | Parapet wrapped in R-10ci | Sample text: A-XXX,
5.5.4 | Fenestration (Prescriptive) | Sample text: Fenestration requirements Elevation showing 95' demarcation | Sample text: Window U-factor below 95 feet Umax-0.30 (fixed) Umax-0.40 (operable) Window U-factor above 95 feet Umax-0.36 (fixed) Umax-0.42 (operable) SHGCmax - 0.36 | Sample text: W-1 (fixed) - installed below 95 feet U-0.28, SHGC - 0.36 W-2 (operable) - installed below 95 feet U-0.40, SHGC - 0.36 W-3 (fixed) - installed 95 feet & above U-0.32, SHGC - 0.36 W-2 (operable) - installed 95 feet & above U-0.40, SHGC - 0.36 | Sample text: A-XXX, EN-XXX (elevation showing 95' demarcation)
5.5.4.2, Table 5.5-4 | Maximum area | Sample text: Window to wall Ratio | Sample text: 40% Maximum | Sample text: 25% | Sample text: A-XX1-XX2 (Building Elevations) Gross wall area and gross window area.
5.5.4.2.3 | Minimum skylight fenestration area | Minimum skylight requirements | Sample text: Total daylight zone under skylights shall be not less than half the floor area. Skylights in office, storage, automotive service, manufacturing, nonrefrigerated warehouse, retail store and distribution/sorting area: Haze factor greater than 90%. | Sample text: Skylights provided on FL-12 above corridors and offices Haze factor 92% for all skylights. | Sample text: A-XXX (daylight zone calculation)
5.5.4.5 | Fenestration Orientation | Fenestration Orientation | AW < (AT)/4 and AE <(AT)/4 AW × SHGCW <(AT × SHGCC)/5 and AE × SHGCE <(AT × SHGCC)/5 | AW= 5000 ft2, AE = 5000 ft2, AT = 30,000 ft2SHGCW = 0.36, SHGCE = 0.36, SHGCC = 0.36 AW < (AT)/4: 5000 < 7,500 AW× SHGCW = 1800< 2160 | Sample text: A-XX1-XX2 (Building Elevations) Gross wall area and gross window area. A-XXX fenestration performance
5.5.4.6, Table 5.5-4 | Visible Transmittance/SHGC Ratio | Minimum VT/SHGC requirements when daylighting controls are required | VT/SHGC > 1.10 | VT = 0.90 SHGC = 0.36 VT/SHGC = 25 | A-XXX fenestration performance
5.8.1.6 | Recessed lighting | Sample text: Recessed luminaires in the thermal envelope to be weather sealed. | Sample text: Recessed luminaires installed in the building thermal envelope shall be sealed to maximum air leakage 2 cfm. | Sample text: Recessed luminaires in the roof ceiling assembly sealed to 1 cfm air movement. | Sample text: A-XXX (Reflected ceiling plan) A-5XX (Schedules) Sealant notes in Comments column of Luminaire schedule.
5.8.1.10 | Multiple layers of continuous insulation | Sample text: Installation of multiple layers of continuous insulation. | Two or more insulation boards in construction assemblies shall be in accordance with Section 5.8.1.10. If the manufacturer does not call for multiple layers the edge joints between each layer of continuous insulation boards shall be staggered. | Sample text: Stagger the edge joints between each layer of continuous insulation boards. | Sample text: A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)

## Com.ASHRAE - HVAC
2020 NYCECC Tabular Analysis Commercial Building in compliance with Appendix CA (Amendments to ASHRAE 90.1-2016)
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, 5.1.3, 6.1.1.3, 6.4.3.10.1, 7.1.1.3, 8.1.4, 9.1.2, and 10.1.1.3.
ASHRAE Citation | Provision | Item Description | Code Prescriptive Value (ASHRAE) | Proposed Design Value | Supporting Documentation
6.4.1.6 | Buildings with high efficiency space heating gas boiler systems | Sample text: Condensing boilers, gas-fired (B-1, B-2) | gas-fired condensing boilers with rated efficiency >90% Et shall be designed to operate in condensing mode. RWT < 120F. | Sample text: Return Water Temp (RWT) = 115F for B-1 and B-2 | Sample text: See mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX, and mechanical details M-XXX
6.4.2.1 | Load calculations | HVAC system sizing | Sample text: Determined in accordance with ANSI/ASHRAE/ACCA Standard 183 HVAC Systems and Equipment Handbook | Sample text: Design loads are determined in accordance with the procedures described in the ANSI/ASHRAE/ACCA Standard183. Specified equipment sized within load calculation limits | Signed and sealed statement from Engineer certifying compliance with Energy Code
6.4.3.1 | Zone Thermostatic controls (Mandatory) | Sample text: Thermostats/humidistats for mechanical zones | Minimum one thermostat/humidistat required per zone | Sample text: One thermostat is provided for each zone | Sample text: Thermostats shown on mechanical plans, M-XX1, M-XX2, M-XX3.
6.4.3.2 | Set point overlap restriction (Mandatory) | Sample text: Heat pump, split unit thermostats | Zone thermostat operation shall have minimum 5 °F dead band between heating and cooling | Sample text: Each thermostat will be programmed as required | Sample text: See mechanical control sequences, drawing M-XXX.
6.4.3.3 | Off-hour controls (Mandatory) | Sample text: All zones | All zone thermostat shall be operated via thermostatic setback controls operated via an automatic time clock or a programmable control system | Sample text: Each thermostat will be programmable to meet requirements | Sample text: See mechanical control sequences, drawing M-XXX.
6.4.3.3.1 | Automatic setback and shutdown (Mandatory) | Sample text: All zones | Controls shall be capable of automatically starting and stopping the systems for seven different daily schedules per week, capable of having settings saved in memory for 10 hours during a loss of power, and a manual system "on" override for up to two hours, or an occupancy sensor | Sample text: Each thermostat will be programmable to meet requirements | Sample text: See mechanical control sequences, drawing M-XXX.
6.4.3.3.3 | Automatic start (Mandatory) | Sample text: All zones | Controls shall be provided for each HVAC system and automatically adjusting the daily start time of the HVAC in order to bring each space to the desired temperature. | Sample text: Each thermostat will be programmable to meet requirements | Sample text: See mechanical control sequences, drawing M-XXX.
6.4.3.3.4 | Zone isolation required (Mandatory) | Sample text: Zone isolation | HVAC systems serving zones that are over 25,000 ft2 in floor area or that span more than one floor and are designed to operate or be occupied nonsimultaneously shall be controlled independently and divided into isolation areas where each area has isolation devices and controls configured to automatically shut off the supply of conditioned and outdoor air to and exhaust air from the isolation area. | Sample text: There are independent controls for each open floor office as specified as Zone 1 and Zone 2 | Sample text: See mechanical plans, M-XX1, M-XX2, M-XX3, mechanical control sequences, drawing M-4XX
6.4.3.3.5 | Automatic control of HVAC systems serving guestrooms (Mandatory) | Sample text: HVAC control in All hotel rooms | In hotels and motels with greater than 50 guest rooms, automatic control for the HVAC equipment and ventilation system serving each guest room shall be configured to setback or turn off when unoccupied. | Sample text: Guest rooms provided with Captive key card system as per requirements. | Sample text: See mechanical details, drawing M-XXX, mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX
6.4.3.4.2 | Shutoff dampers (Mandatory) | Sample text: Outdoor air intake, exhaust openings, stairway and shaft vents | Each outdoor supply air and exhaust air ducts shall be provided with motorized dampers to shut off or open as required by this section. Class I motorized damper with a maximum air leakage rate of 4cfm/ft2 of damper surface area at 1.0 inch water gauge. | Sample text: Class I motorized damper with a maximum air leakage rate of 4cfm/ft2 of damper surface area at 1.0 inch water gauge | Sample text: See mechanical plans, M-XX1, M-XX2, M-XX3, mechanical control sequences, drawing M-4XX
6.4.3.4.5 | Enclosed parking garage ventilation controls (Mandatory) | Sample text: Enclosed parking garage ventilation control requirements | Shall have contamination-sensing devices and automatic controls configured to stage fans or modulate fan average airflow rates to 50% or less of design capacity, or intermittently operate fans less than 20% of the occupied time or as required to maintain acceptable contaminant levels in accordance with NYC MC | Sample text: Enclosed parking garage fan equipped with VFD controls as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.4.3.5 | Heat pump auxiliary heat control | Sample text: 3 ton packaged heat pump with electrical heat, HP-1 | Except during defrost, supplementary electric heat to be prevented from coming on when heat pump can meet load | Sample text: Electric heat shall be enable only when the heat pump cannot meet load. | Sample text: See mechanical control sequences, drawing M-XXX.
6.4.3.7 | Freeze protection and Snow- and ice-melt system controls | Sample text: Snow- and ice-melt system at carport | Freeze protection systems shall include automatic controls shall shut off the systems when outdoor air temperatures are above 40°F or when the conditions of the protected fluid will prevent freezing | Sample text: Heat tracing of outdoor piping shall include automatic controls that shut off the systems when outdoor temperatures are above 40°F or when the conditions of the protected fluid will prevent freezing | Sample text: See mechanical plans, M-XX1, M-XX2, M-XX3, mechanical control sequences, drawing M-4XX
6.4.3.8 | Ventilation controls for high occupancy areas | Sample text: RTU-1, DCV system in auditorium | Required in spaces greater than 500 square feet and occupant density of 25 people per 1000 square feet or greater | Sample text: RTU-1 includes a DCV system provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.4.3.9 | Heated or cooled vestibules (mandatory) | Sample text: Entrance vestibule heating/cooling | heated vestibules to shut off when outdoor air temperature > 45F Heating setpoint <60F Cooling setpoint >85F | Sample text: Programmable thermostat in vestibule limits temperature to the code required setpoints. | Sample text: Thermostats shown on mechanical plans, M-XX1, M-XX2, M-XX3. See mechanical control sequences, drawing M-XXX.
6.4.3.10 | Direct Digital Control (DDC) Requirements | Sample text: DDC controls on boilers and cooling tower | DDC controls as per 6.4.3.10 | Sample text: BMS system provided meeting requirements of 6.4.3.10 | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.4.3.11 | Chilled-water Plant Monitoring | Sample text: Chiller plant controls | Chiller plant controls per 6.4.3.11 | Sample text: BMS system provided meeting requirements of 6.4.3.11 | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.4.3.12 | Economizer fault detection and diagnostics (Mandatory) | Sample text: RTU-1, Economizer fault detection and diagnostics | Air-cooled unitary direct-expansion units and VRF units which have an economizer must include a fault detection and diagnostics system which complies with items 1-7 listed in 6.4.3.12 | Sample text: RTU-1 includes economizer with fault detection and diagnostic controls, per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.4.4.1.1 | Protection of piping insulation (Mandatory) | Sample text: Piping located outdoors | All piping insulation is protected from damage, including that due to sunlight, moisture, equipment maintenance and wind. Adhesive tape is not permitted. | Sample text: All outdoor piping insulation is protected from damage by using (XXXX - type of material). | Sample text: See mechanical drawing M-XXX
6.4.4.1.2, Table 6.8.2 | Duct and plenum insulation | Sample text: All ductwork | Supply and return ducts and plenums in shall have a minimum of R-6 where located in unconditioned spaces and R-8 minimum where located outside the building. Where located within a building envelope assembly, the duct or plenum shall be separated from the building exterior or unconditioned or exempt spaces by a minimum of R-8. | Sample text: Unconditioned spaces: R-6 Conditioned spaces: None, exterior wall insulated >R-8 | Sample text: See mechanical drawing M-XXX
6.4.4.1.3, Table 6.8.3 | Piping Insulation | Sample text: Boiler piping insulation, mini-split refrigerant insulation | Sample text: Boiler piping insulation: 105-140F, 1-1.5" diameter = 1.0 inches Refrigerant insulation: <40F, < 1" diameter = 0.5 inches | Sample text: Boiler piping insulation: 1.5 inches Refrigerant insulation: 0.5 inches | Sample text: See mechanical drawing M-XXX
6.4.4.2.1 | Duct Sealing | Sample text: Ductwork sealing | All ducts shall be sealed according to requirements | Sample text: All low pressure ducts properly sealed as per requirements | Sample text: See mechanical drawing M-XXX
6.4.4.2.2 | Duct Leakage Test | Sample text: High Pressure Ductwork | Ducts operating in excess of 3" W.G. shall be insulated and sealed per 6.4.4.2 and leak tested per code requirements with a rate of air leakage (CL) less than or equal to 4.0 | Sample text: all high pressure ducts sealed as per requirements and insulated to R-8. All ducts leak tested to < 4.0, per Equation 4-8 | Sample text: See mechanical drawing M-XXX
6.4.5, 6.4.6, 6.5.11 | Walk-in coolers, freezers and refrigerated display cases | Sample text: Refrigeration systems | Refrigerated display cases, walk-in coolers or walk-in freezers that are served by remote compressors and remote condensers not located in a condensing unit, shall comply with Sections 6.4.5 and 6.4.6 | Sample text: Refrigeration systems provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.1 | Economizers (Prescriptive) | Sample text: Economizers on RTU-1, RTU-2 | Air Economizer required for all cooling systems, unless an exception is met | Sample text: Economizer not required PTAC-1 through PTAC-5, Item 3 Individual cooling unit < 270,000 BTU/h Economizer not required VRF-1 through VRF-5, exception 5 Minimum eff. Table C403.3.2(11): 11.0 EER High eff. exemption limit: 13.2 EER Proposed VRF: 13.5 EER | Sample text: See mechanical schedule, M-4XX
6.5.1.1 | Air economizers | Sample text: Air economizers, RTU-1 | Air economizers shall be configured to provide up to 100% of design supply air quantity as outdoor air for cooling. Economizer controls/dampers configured to sequence dampers with the cooling equipment. Fixed dry-bulb control, high limit shutoff when outdoor air Temp > 65. Systems capable of relieving excess outdoor air during economizer operation. | Sample text: Air economizer system controls, As per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.1.2 | Fluid economizers | Sample text: Fluid economizer, WSHP-1 through WSHP-5 | Fluid economizers shall be configured to cool supply air and provide 100% of expected cooling load at outdoor air temp <50Fdb, <45Fwb. Fluid economizer system shall have water-side pressure drop of < 15 feet OR a secondary loop | Sample text: Water economizer systems controls provided as per requirements. | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.1.3 | Integrated economizer control | Sample text: Economizer control on RTU-1, RTU-2 | Economizer systems shall be integrated with the mechanical cooling system and be capable of providing partial cooling even where additional mechanical cooling is required to provide the remainder of the cooling load. Controls shall not be capable of creating a false load in the mechanical cooling systems by limiting or disabling the economizer or any other means, except at the lowest stage of mechanical cooling. | Sample text: Economizers systems are integrated with the mechanical cooling system and capable of providing partial cooling, per control sequence | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.1.4 | Economizer heating system impact | Sample text: Economizer heating system impact | Economizer operation does not increase building heating energy use during normal operation | Sample text: Economizer operation does not increase building heating energy use during normal operation | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.2.2.1 | Three-pipe System | Sample text: Three Pipe Systems | Hydronic systems using a common return for both hot water and chilled water are prohibited | Sample text: Not applicable | Sample text: These systems are not used
6.5.2.2.2 | Two-pipe Changeover System | Sample text: Two Pipe Changeover | Dead band for change-over is a minimum of 15 degrees F based on O.A., minimum operation in one mode for 4 hours before changeover, heating and cooling supply temperature no more than 30 degrees F apart at change-over point. | Sample text: Dead band controls as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.2.2.3 | Hydronic (Water Loop) Heat Pump Systems | Sample text: Water loop heat pump system controls | Minimum 20 degree F dead band between initiation of heat injection or heat rejection to water loop. Open circuit cooling tower on primary/secondary loop | Sample text: Heat pump system controls as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.2.6 | Ventilation air heating control ( Mandatory) | Sample text: RTU-1 | Units that provide ventilation air and operate in conjunction with heating/cooling systems shall not warm supply air to greater than 600F when majority of zones require cooling. | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.3.1.1, table 6.5.3.1-2 | Allowable Fan Horsepower | Sample text: Exhaust Fans, TX-1 through TX-5, KX-1 through KX-5 | Total system fan hp shall not exceed limits in Table 6.5.3.1-1 | Sample text: Total Fan power = XXX bhp | Sample text: See mechanical details, drawing M-XXX
6.5.3.1.2 | Motor nameplate horsepower | Sample text: Exhaust Fans, TX-1 through TX-5, KX-1 through KX-5 | Motor selection does not exceed 1.5xbhp for fans less than 6bhp | Sample Text: Fan hp < 8 hp hp = 1.5 * 5.5bhp | Sample text: See mechanical details, drawing M-XXX
6.5.3.1.3 | Fan Efficiency | Sample text: Fan efficiency for AHU-1, 2, 3 | Minimum FEG = 67 | Sample text: Minimum FEG = 70 | Sample text: See mechanical details, drawing M-XXX
6.5.3.2.1 | Fan Airflow control | Sample text: Fan controls for single-zone DX cooling system 135kBTU/h | Supply fans controlled by variable speed drives and configured to requirements in 6.5.3.2. | Sample text: Variable speed fan controls provided per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.3.2.2 | VAV Static pressure sensor location | Sample text: VAV fans | Static pressure sensors used to control VAV fans shall be located such that the controller set point is not greater than 1.2 inches w.c.. Where this results in one or more sensors being located downstream of major duct splits, not less than one sensor shall be located on each major branch to ensure that static pressure can be maintained in each branch. | Sample text: Static sensor used to control VAV fans shall be as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.3.3 | Multiple zone VAV system ventilation optimization control | Sample text: Multi zone systems with DDC of zone boxes | Control system shall have automatic controls configured to reduce OA intake flow below design rates in response to changes in system ventilation efficiency | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.3.4 | Parallel-flow fan-powered VAV air terminal control | Sample text: Parallel-flow fan-powered VAV controls | Parallel-flow fan-powered VAV controls have automatic controls configured to: 1. terminal fan is off when space heating is required or where required for ventilation 2. Turn on terminal fan as first stage of heating before heating coil is activated 3. During heating for warmup or setback temperature control, operate terminal fan and heating coil without primary air | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.3.5 | Supply-air temperature reset controls | Sample text: HVAC system serving zones 5-XX | Control system shall automatically reset supply-air temperature in response to building load or outdoor air temperature. The controls shall be capable of resetting the supply air temperature not less than 25% of the difference between the design supply-air temperature and the design room air temperature. | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.3.6 | Fractional hp fan motors (Mandatory) | Sample text: Fractional hp fan motors | Motor fans 1/12 hp to 1 hp shall be electronically commutated motors or have a minimum efficiency of 70% and must have the means to adjust motor speed for either balancing or remote control. The use of belt-driven fans to sheave adjustments for airflow balancing instead of varying motor speed are permitted. | Sample text: Motor fan 1 hp and efficiency 70% | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.3.7 | Ventilation Design | Sample text: Ventilation cfm and Outdoor air control | Mechanical ventilation is provided in accordance with NYC MC Chapter 4. The minimum design airflow rate does not exceed the minimum by more than 135%. | Sample text: NYC MC, minimum outdoor air = 60cfm, | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.4.1 | Boiler turndown | Sample text: Boilers B-1, B-2 turndown controls | Boiler systems with design input greater than 1,000,000 Btu/h shall comply with the turndown ratio specified in Table 6.5.4.1. | Sample text: Boiler B-1, B2 each have 7 to 1 turndown ratio | Sample text: See mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX, and mechanical details M-XXX
6.5.4.2 | Hydronic variable flow system | Sample text: Boilers B-1, B-2 reset controls | Chilled water pumps > 5 hp and hot water pumps > 10hp have variable flow systems and meet the requirements of this section | Sample text: Hot water pump controls provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.4.3 | Chiller and boiler isolation | Sample text: Pumps CW-1 , HW-1 | Chilled water plants including more than one chiller shall have the capability to reduce flow automatically through the chiller plant when a chiller is shut down. Chillers piped in series for the purpose of increased temperature differential shall be considered as one chiller. Boiler plants including more than one boiler shall have the capability to reduce flow automatically through the boiler plant when a boiler is shut down. | Sample text: Pumps CW-1, HW-1 equipped with VFD controls as per requirements | Sample text: See mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX, and mechanical details M-XXX
6.5.4.4 | Chilled- and Hot-Water Temperature Reset Controls | Sample text: Boilers B-1, B-2 reset controls | Hydronic systems greater than or equal to 300,000 Btu/h in design output capacity supplying heated or chilled water to comfort conditioning systems shall include controls in this section. | Sample text: Boiler controls provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.4.5 | Hydronic (water loop) heat pumps and water-cooled unitary equipment | Sample text: Two-position valve and pump controls for WSHP 1,2 | Each hydronic heat pump equipped with two-position valve. Total pump system power exceeding 5 hp shall have variable flow. | Sample text: WSHP 1,2 controls provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.4.6 | Pipe sizing | Sample text: condensing water piping design | Sample text: 4" condenser water piping, operating >4400 hrs/year, maximum 320 GPM for variable flow | Sample text: 4" condenser water piping, designed for 300 GPM with variable flow | Sample text: See mechanical schedule, M-4XX,
6.5.5 | Heat rejection equipment | Sample text: Cooling Towers, CT-1, CT-2 | Fans shall be able to operate at 2/3 speed or less, and have controls to adjust fan speed based on demand | Sample text: Fans on CT-1, CT-2 equipped with VFD controls per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.6.1 | Energy recovery ventilation systems (Mandatory) | Sample text: MAU-1, energy recovery wheel | Required in systems with design air capacity and (%) outdoor air at full design flow rate shown in Tables 6.5.6.1-1 and 6.5.6.1-2. Minimum 50% total effectiveness. | Sample text: Energy recovery wheel provided with 65% efficacy and economizer bypass | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.6.2 | Heat Recovery for Service Water Heating | Sample text: Water cooled Chiller plant = 2 million BTU/h | Provide condenser water heat recovery, required for 24 hr/day operations, with water cooled systems over 6 million btu/h | Sample text: not applicable | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.7.2 | Kitchen exhaust systems (Mandatory) | Sample text: Kitchen exhaust systems | Replacement air introduced directly into the hood cavity of kitchen exhaust hoods shall not exceed 10% of the hood exhaust airflow rate. Conditioned supply air delivered to any space shall not exceed the greater of the items listed in this section of this code | Sample text: Kitchen exhaust system provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.5.8 | Radiant heating system | Sample text: Parking Garage heating | All heating systems installed outdoors shall be of the radiant type, with an occupancy switch or timer switch. | Sample text: Radiant heat system provided as per requirements | Sample text: See mechanical details, drawing M-XXX, mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX
6.5.9 | Hot Gas Bypass Limitation | Sample text: 75kbtu/h unitary package | Hot gas bypass is allowed only on systems with multiple steps of unloading or continuous capacity modulation. Allowed Bypass capacity per Table C403.3.3 | Sample text: All cooling systems do not use hot gas bypass | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
6.7.2.3 | Mechanical, renewable energy, and service water heating systems commissioning and completion requirements | Sample text: Commissioning | Mechanical systems shall be commissioned and completed in accordance with Section C408 | Sample text: Total building heating capacity = 750,000 BTU/h Total cooling capacity = 620,000 BTU/h Commissioning is required for this project per requirements | Sample text: See mechanical drawing M-XXX
Table 6.8.1-1 | Minimum efficiency requirements: electrically operated unitary air conditioners and condensing units | Sample text: (1) Split System 7.5 ton air cooled AC unit, AC-1 Sample text: (1) new air cooled condensing unit, 150,000 Btu/, C-1 | Sample text: 11.2 EER , 12.9 IEER (AC-1) Sample text: 10.5 EER, 11.8 IEER (C-1) | Sample text: 12.0 EER, 13.5 IEER (AC-1) Sample text: 11.1 EER, 12.2 IPLV (C-1) | Sample text: Split System AC units schedule, drawing M-XXX Sample text: Condensing units schedule, drawing M-XXX
Table 6.8.1-2 | Minimum efficiency requirements: electrically operated unitary and applied heat pumps | Sample text: PTAC (Cooling Mode) New construction, 12,000 BTU/h, PTAC-1 | Sample text: 14.0 - (0.300 x Cap/1000) = 10.4 EER | Sample text: 10.5 EER | Sample text: PTAC AC units schedule, drawing M-XXX
Table 6.8.1-3 | Water chilling packages - efficiency requirements | Sample text: new air cooled chiller, 200 ton | Sample text: PATH A: >10.1 EER @ Full load, 14.0 IPLV OR PATH B: >9.7 EER @ Full load, 16.1 IPLV | Sample text: 10.2 EER @ Full load, 15 IPLV | Sample text: Chiller schedule, drawing M-XXX
Table 6.8.1-4 | Minimum efficiency requirements: electrically operated PTACs, PTHPs, Single-package vertical AC, Single-package vertical HP, Room AC, and Room AC-HPs | Sample text: Room AC w/ louvered slides, 8,000 BTU/h, RAC-1 | Sample text: 10.9 CEER | Sample text: 10.9 CEER | Sample text: Room AC units schedule, drawing M-XXX
Table 6.8.1-5 | Warm-air furnaces and combination warm-air furnaces/air-conditioning units, warm-air duct furnaces and unit heaters, minimum efficiency requirements | Sample text: new warm-air furnace, gas fired 250,000 BTU/h, RTU-1 | Sample text: 80% Et | Sample text: 81% Et | Sample text: Furnace units schedule, drawing M-XXX
Table 6.8.1-6 | Minimum efficiency requirements: gas- and oil-fired boilers | Sample text: Gas fired, hot-water boiler 500,000 Btu/h input, B-1 | Sample text: 80% Et | Sample text: 83% Et | Sample text: Boiler schedule, drawing M-XXX
Table 6.8.1-7 | Minimum efficiency requirements: heat rejection equipment | Sample text: new axial fan open circuit cooling tower, 200 tons | Sample text: 40.2 gpm/hp | Sample text: 40.2 gpm/hp | Sample text: Chiller schedule, drawing M-XXX
Table 6.8.1-8 | Heat Transfer Equipment | Sample text: Liquid-to-liquid heat exchanger | Sample text: minimum efficiency not required, tested to AHRI 400 | Sample text: minimum efficiency not required, tested to AHRI 400 | Samples text: Equipment schedule, drawing M-XXX
Table 6.8.1-9 | Minimum efficiency requirements: electrically operated variable-refrigerant-flow air conditioners | Sample text: VRF air cooled air conditioner, 72,000 Btu/h (condenser capacity) | Sample text: 11.2 SEER, 15.5 IEER | Sample text: 11.5 SEER, 18.1 IEER | Samples text: VRF equipment schedule, drawing M-XXX
Table 6.8.1-10 | Minimum efficiency requirements: electrically operated variable-refrigerant-flow air-to-air and applied heat pumps | Sample text: VRF heat pump, without heat recovery, 72,000 Btu/h (condenser capacity) | Sample text: 11.0 EER, 14.6 IEER (cooling) 3.3 COPH (heating) | Sample text: 11.5 EER, 18.1 IEER (cooling) 3.5 COPH (heating) | Samples text: VRF equipment schedule, drawing M-XXX
Table 6.8.1-13 | Refrigeration equipment performance | Sample text: Minimum efficiency requirements for commercial refrigeration and commercial refrigerators and freezers | Refrigeration equipment shall have an energy use in kWh/day not greater than the values of Tables C403.10.1(1) and C403.10.1(2) | Sample text: Commercial refrigerators provided as per requirements | Sample text: See mechanical details, drawing M-XXX, mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX

## Com.ASHRAE - Lighting Power
2020 NYCECC Tabular Analysis Commercial Building in compliance with Appendix CA (Amendments to ASHRAE 90.1-2016)
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, 5.1.3, 6.1.1.3, 6.4.3.10.1, 7.1.1.3, 8.1.4, 9.1.2, and 10.1.1.3.
ASHRAE Citation | Provision | Item Description | Code Prescriptive Value (ASHRAE) | Proposed Design Value | Supporting Documentation
9.2.2.3, Table 9.5.1, Table 9.6.1 | Interior lighting power requirements | Sample text: Interior lighting power requirements | Sample text: Open Office: 0.78 W/SF Conf Rm: 0.93 W/SF Stairwell: 0.50 W/SF Restroom: 0.75 W/SF The total connected interior lighting power shall be determined in accordance with Equation 4-10. | Sample text: Open Office: 0.68 W/SF Conf Rm: 0.92 W/SF Stairwell: 0.43 W/SF Restroom: 0.60 W/SF LPD value for building is less than the interior lighting power calculated under Section C405.3.2. See drawing EN-XXX. | Sample text: see drawing EN-XXX (Lighting fixture schedules)
9.4.1 | Lighting controls (Mandatory) | Sample text: interior lighting controls include occupancy sensors, daylight responsive controls, bi-level controls, and automatic shut-off | Lighting systems shall be provided with controls as specified in Sections 9.4.1.1. | Sample text: Occupancy sensors in restrooms, conference rooms, open offices; daylight responsive controls in all offices; bi-level controls in stairwells; automatic shut-off via BMS for all lighting | Sample text: see drawing EN-XXX (Lighting fixture schedule & narratives)
9.4.1.1(a) | Local controls | Sample text: Manual controls | Sample text: There shall be one or more manual lighting controls in the space that controls all of the lighting in the space. Each control device shall control an area (1) no larger than 2500 ft2 if the space is 10,000 ft2 and (2) no larger than 10,000 ft2 otherwise. The device installed to comply with this provision shall be readily accessible and located so that the occupants can see the controlled lighting when using the control device. | Sample text: Manual controls in each space | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
9.4.1.1(b) | Restricted to manual ON | Sample text: Vacancy sensors | Sample text: Lighted shall be turned on with manual control | Sample text: Vacancy sensors with Manual ON provided in all bathrooms and private offices | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
9.4.1.1(c) | Restricted to partial ON | Sample text: Occupancy sensors | Sample text: No more than 50% of the lighting power for the general lighting shall be allowed to be automatically turned on, and none of the remaining lighting shall be automatically turned on. | Sample text: Vacancy sensors with Manual ON provided in all bathrooms and private offices | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
9.4.1.1(d) | Bi-level lighting controls | Sample text: Bi-level controls | The general lighting in the space shall be controlled so as to provide at least one intermediate step in lighting power or continuous dimming in addition to full ON and full OFF. At least one intermediate step shall be between 30% and 70% (inclusive) of full lighting power. | Sample text: Bi-level controls provided in open space on 5th floor. | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
9.4.1.1(e) | Automatic daylight responsive controls for sidelighting | Sample text: Daylight-responsive controls. | Daylight responsive controls complying with 9.4.1.1.e shall be provided to control the electric lights within primary and secondary daylight zones. General lighting in the secondary sidelighted area shall be controlled independently of the general lighting in the primary sidelighted area. | Sample text: Daylight responsive controls provided in all office areas pre requirements | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
9.4.1.1(f) | Automatic daylight responsive controls for toplighting | Sample text: Daylight-responsive controls under skylights. | Daylight responsive controls complying with 9.4.1.1.f shall be In any space where the combined input power for all general lighting completely or partially within daylight area under skylights and daylight area under roof monitors is 100 W or greater, general lighting in the daylight area shall be controlled by photocontrols. . | Sample text: NA - Total wattage less than 100 W | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
9.4.1.1(g) | Automatic partial off | Sample text: Occupancy sensors | The general lighting power in the space shall be automatically reduced by at least 50% within 15 minutes of all occupants leaving the space. | Sample text: Occupancy sensors reducing light by 50% in all corridors and stairwells | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
9.4.1.1(h) | Automatic full off | Sample text: Occupancy sensors | All lighting, including lighting connected to emergency circuits, shall be automatically shut off within 15 minutes of all occupants leaving the space. A control device meeting this requirement shall control no more than 5000 ft2, provided that for open plan office spaces or dining spaces a control device meeting this requirement shall control not greater than 600 ft2 | Sample text: Occupancy sensors with full-off in all open plan offices | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
9.4.1.1(i) | Scheduled shut-off | Sample text: Time-switch controls at room XX-X | All lighting in the space, including lighting connected to emergency circuits, shall be automatically shut off during periods when the space is scheduled to be unoccupied using either (1) a time-of-day operated control device that automatically turns the lighting off at specific programmed times or (2) a signal from another automatic control device or alarm/security system. The control device or system shall provide independent control sequences that (1) control the lighting for an area of no more than 25,000 ft2, (2) include no more than one floor, and (3) shall be programmed to account for weekends and holidays. Any manual control installed to provide override of the scheduled shutoff control shall not turn the lighting on for more than two hours per activation during scheduled off periods and shall not control more than 5000 ft2. | Sample text: Time-switch controls provided as required. | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
9.4.1.2 | Parking Garage Lighting Control | Sample text: Parking garage lighting controls | 1. Parking garage lighting shall have automatic lighting shutoff per Section 9.4.1.1.(i). 2. Lighting power of each luminaire shall be automatically reduced by a minimum of 30% when there is no activity detected within a lighting zone for 15 minutes. Lighting zones for this requirement shall be no larger than 3600 ft2. 3.Lighting for covered vehicle entrances and exits from buildings and parking structures shall be separately controlled by a device that automatically reduces the lighting by at least 50% from sunset to sunrise. 4. The power to luminaires within 20 ft of any perimeter wall structure that has a net opening-to-wall ratio of at least 40% and no exterior obstructions within 20 ft, shall be automatically reduced in response to daylight by at least 50%. | Sample text: Lighting controls in parking garage per requirements | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
9.4.1.3 | Specific application controls. | Sample text: Retail display case lighting | Specific application controls shall be provided for the following: 1. Display and accent light shall be controlled by a dedicated control that is independent of the controls for other lighting within the room or space. 2. Sleeping units have controls to automatically switch off all luminaires and switched receptacles within 20 minutes 3. Permanently installed luminaires within dwelling units have time-switch or light reduction controls 4. Nonvisual applications shall be controlled by a time-switch that is independently controlled from the general lighting in the room or space | Sample text: Display and accent light D4 to D9 shall be controlled by a dedicated control that is independent of the controls for other lighting within the room or space. | Sample text: see drawing EN-XXX
9.4.1.4 | Exterior lighting controls | Sample text: Exterior lighting controls | Exterior lighting system shall be provided with controls that comply with the following: 1. Lights shall be automatically turned off when daylight is present and satisfies the lighting needs 2. Building façade lighting and landscape lighting shall shut off not later than 1 hour after business closing to not earlier than 1 hour before business opening OR shall be controlled so the total wattage is reduced by not less than 50% by shutting off the lighting or dimming luminaires 3. Time switch controls shall have a clock capable of programming for >7 days, and being set for 7 different day types per week, have an automatic holiday setback feature, and have backup capabilities | Sample text: Lighting on the north building facade equipped with photosensors. See lighting Plan. | See drawing EN-XXX
9.4.1.4(b) | Exterior decorative lighting controls | Sample text: Exterior decorative lighting controls | Building façade lighting and landscape lighting shall shut off not later than 1 hour after business closing to not earlier than 1 hour before business opening OR shall be controlled so the total wattage is reduced by not less than 50% by shutting off the lighting or dimming luminaires | Sample text: Lighting on the south building facade equipped with dimmable controls set to 50% power. See lighting Plan. | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
9.4.1.4(d) | Outdoor parking area lighting controls | Sample text: Outdoor parking lighting controls | Luminaires having rated input wattage > 78 W and a mounting height < 24 feet shall be controlled to automatically reduce the power by a minimum of 50% when no activity is detected for 15 min or less. No more than 1500 W of lighting power shall be controlled together. | Sample text: Outdoor parking area lighting poles are equipped with occupancy sensors, per requirements. | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
9.4.2 | Exterior lighting power requirements (Mandatory) | Sample text: Total connected load of proposed exterior lighting for lighting zone 3 | Sample text: 10.21 kW The exterior lighting power allowance shall be determined in accordance with Section C405.5.1. | Sample text: 7.66 kW The total exterior lighting power is less than the exterior lighting power calculated under Section C405.4. See drawing EN-XXX. | Sample text: A-XXX drawings (Reflected Ceiling Plans for all floors) E-XXX drawings (Reflected Ceiling Plans for all floors) E-XXX - XXX (Fixture schedule, control narrative, and details)
9.4.4 | Dwelling Unit Lighting | Sample text: Dwelling unit lighting fixtures | Not less than 90% of the lamps in permanently installed lighting fixtures shall use lamps with an efficacy of at least 65 lumens per watt, or have a total luminaire efficacy of at least 45 lumens per watt. | Sample text: All lamps in fixtures are 68 lumens per watt. | Sample text: see drawing E-XXX (Lighting fixture schedules)
9.4.5 | Exit signs | Sample text: Exit signs | Internally illuminated exit signs shall not exceed 5 W per face. | Sample text: All exit signs 2W per face. | Sample text: see drawing E-XXX (Lighting fixture schedules)
9.6.2 | Additional interior lighting power | Sample text: Decorative display lighting | Sample text: a. For spaces in which lighting is specified to be installed in addition to the general lighting for the purpose of decorative appearance or for highlighting art or exhibits not exempted in Section 9.2.2.3, Exception 1, provided that the additional lighting power shall not exceed 0.75 W/ft2 of such spaces. | Sample text: Additional 0.75 W/sf for display lighting in lobby | Sample text: see drawing E-XXX (Lighting fixture schedules)
9.7.3 | System commissioning | Sample text: Commissioning for lighting controls | Sample text: All lighting controls required to perform commissioning and functional testing | Sample text: Commissioning required | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
8.4.2 | Automatic receptacle controls | Sample text: receptacle control for office spaces | Sample text: a. At least 50% of all 125 V, 15 and 20 amp receptacles in all private offices, conference rooms, rooms used primarily for printing and/or copying functions, break rooms, classrooms, and individual workstations. | Sample text: 50% of receptacles in office spaces shut-off after 6pm | Sample text: See drawing EN-XXX.
8.4.3.1 | Electrical Energy Monitoring | Whole building electrical metering | Sample text: Measurement devices shall be installed to monitor the electrical energy use in each of the following: 1. Total energy 2. HVAC systems 3. Interior Lighting 4. Exterior Lighting 5. Receptacle Circuits | Sample text: Submetering devices for HVAC systems, interior lighting, exterior lighting, and all electrical energy. See mechanical plans/electrical plans. | Sample text: See drawing EN-XXX.
8.4.3.2 | Electrical Energy Monitoring - Recording and reporting | Whole building electrical metering | Sample text: Measurement devices shall be installed to record electrical energy us every 60 minutes. | Sample text: Submetering devices for HVAC systems, interior lighting, exterior lighting, and all electrical energy. See mechanical plans/electrical plans. | Sample text: See drawing EN-XXX.
8.4.4 | Electrical transformers (Mandatory) | Sample text: Electrical transformers | Electric transformers shall meet the minimum efficiency requirements of Table 8.4.4 | Sample text: Impedance transformers are exempted as per Exception # 8. | Sample text: See drawing EN-XXX for notes.
8.4.6 | Electrical meter (Mandatory) | Sample text: Separate electrical meters have been provided for each dwelling unit. | Each dwelling unit located in a Group R-2 building shall have a separate electrical meter. | Sample text: meter at unit XXX through XXX | Sample text: See note in general notes (EN-XXX).
10.4.1 - Other equipment | Electrical motors (Mandatory) | Sample text: Electrical motors | Electric motors shall meet the minimum efficiency requirements of Tables 10.8-1 through 10.8-5 when tested and rated in accordance with the DOE 10 CFR 431. The efficiency shall be verified through certification under an approved certification program or, where a certification program does not exist, the equipment efficiency ratings shall be supported by data furnished by the motor manufacturer. | Sample text: Electric motors are in compliance as per 10.4.1. See motor manufacturer data on drawing E-XXX. | Sample text: See drawing EN-XXX.
10.4.3.5 | Power conversion systems | Sample text: Elevators | New traction elevators with a rise of 75 feet or more shall have a power conversion system that complies with 10.4.3.5 | Sample text: Regenerative drives for elevators | Sample text: See drawing EN-XXX.
10.4.4 | Escalators and moving walks | Sample text: Escalators | An escalator designed either for one-way down operation only or for reversible operation shall have a variable frequency regenerative drive that supplies electrical energy to the building electrical system when the escalator is loaded with passengers whose combined weight exceeds 750 pounds. | Sample text: Regenerative drives and occupancy sensors provided for escalators | Sample text: See drawing EN-XXX.
10.4.5.1 | Whole building energy monitoring | Whole building fuel metering | Sample text: Measurement devices shall be installed to individually monitor the energy use in each of the following types of energy supplied by a utility, energy provider, or plant that is not with the building: 1. natural gas 2. fuel oil 3. propane 4. steam 5. chilled water 6. hot water | Sample text: Whole building meters provided for Natural gas. See mechanical plans/electrical plans. | Sample text: See drawing EN-XXX.
10.4.5.2 | Whole building electrical monitoring | Whole building electrical metering | Sample text: Measurement devices shall be installed to record electrical energy us every 60 minutes. | Sample text: Whole building meter provided for electricity. See mechanical plans/electrical plans. | Sample text: See drawing EN-XXX.
10.4.6 | Commercial kitchen equipment | Sample text: Kitchen equipment in cafeteria | Sample text: Standard Open Deep-Fat gas Fryer: >50% heavy load cooking energy efficiency, <9,000 Btu/h Idle energy rate | Sample text: Standard Open Deep-Fat gas Fryer: >50% heavy load cooking energy efficiency, <9,000 Btu/h Idle energy rate | Sample text: See drawing EN-XXX.

## Com.ASHRAE - Add'l Eff App I
2020 NYCECC Tabular Analysis Commercial Building in compliance with Appendix CA (Amendments to ASHRAE 90.1-2016)
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, 5.1.3, 6.1.1.3, 6.4.3.10.1, 7.1.1.3, 8.1.4, 9.1.2, and 10.1.1.3.
ASHRAE Citation | Provision | Item Description | Code Prescriptive Value (ASHRAE) | Proposed Design Value | Supporting Documentation
I1.1 | Requirements (for ADDITIONAL EFFICIENCY PACKAGE OPTIONS) | Sample text: Choose one of six additional efficiency options | Buildings shall comply with at least one of the following: 1. More efficient HVAC performance in accordance with Section I2. 2. Reduced lighting power density system in accordance with Section I3. 3. Enhanced digital lighting controls in accordance with Section I4. 4. Provision of a dedicated outdoor air system with energy recovery ventilation for certain HVAC equipment in accordance with Section I5. 5. High-efficiency service water heating in accordance with Section I6. 6. Enhanced envelope performance in accordance with Section I7 | Sample text: Reduced lighting power density system in accordance with Section I3. | Sample text: See note on EN-XXX
I2 | More efficient HVAC equipment performance | More efficient HVAC equipment performance | Sample text: Equipment exceeds code min. by 10%: 1 MBTU/hr gas-fired, hot water boiler @ 80% Et, 300 ton air-cooled chiller @ 10.1 EER, 14 IPLV | Sample text: 1000 MBH gas-fired, hot water boiler @ 96% Et, 300 ton air-cooled chiller @ 12 EER, 16 IPLV | Sample text: See Mechanical schedule, drawing M-XXX
I3 | Reduced lighting power density | Reduced lighting power density | Sample text: Lighting exceeds code min. by 10%: Building Area Method Office: 0.69 W/SF | Sample text: Building Area Method Office: 0.50 W/SF | Sample text: See RCPs, Lighting Schedule, LPD calculation, drawing A-XXX, EN-XXX
I4 | Enhanced digital lighting controls | Enhanced digital lighting controls | Interior lighting in the building shall have enhanced lighting controls that shall be located, scheduled and operated in accordance with Section 9.4.1.1(i) and I4. | Sample text: Office and lobby lighting provided as per requirements | Sample text: See RCPs, Lighting Schedule, LPD calculation, drawing A-XXX, EN-XXX
I5 | Dedicated outdoor air system | Dedicated outdoor air system with energy recovery | Buildings covered by Section6.5 shall be equipped with an independent ventilation system designed to provide not less than the minimum 100 percent outdoor air to each individual occupied space, as specified by the New York City Mechanical Code, and be equipped with an energy recovery system. | Sample text: MAU-1 provides 100% outside air provided to all occupied space and is equipped with an Energy Recovery device | Sample text: See Mechanical schedule, drawing M-XXX
I6 | Reduced energy use in service water heating | Reduced energy use in service water heating | At least 60% of the domestic hot water is provided by waste-heat recovery. Buildings shall be of the following types to use this compliance method: 1. Group R-I: Boarding houses, hotels or motels. 2. Group 1-2: Hospitals, psychiatric hospitals and nursing homes. 3. Group A-2: Restaurants and banquet halls or buildings containing food preparation areas. 4. Group F: Laundries. 5. Group R-2: Buildings with residential occupancies. 6. Group A-3: Health clubs and spas. | Sample text: 75% of DHW load provided by waste-heat from Cogeneration system *As a motel, Group R-1 building, this project complies to use this method. | Sample text: See Mechanical schedule, drawing M-XXX, EN-XXX
I7 | Enhanced envelope performance | Enhanced envelope performance | The thermal performance of the envelope shall demonstrate a minimum 15 % improvement compared to the requirements of Section I7. | Sample text: Total UA 18% improvement beyond code minimum | Sample text: EN-100 sheet
I8 | Reduced air infiltration | Reduced air infiltration | Must show compliance through testing to no more than 0.25 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Building thermal envelope to be tested to no more than 0.4 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Sample text: EN-100 sheet